BLADDER TANK ORIZONTAL PENTRU SPUMA CU MEMBRANA CERTIFICAT UL

UL LISTED HORIZONTAL FOAM BLADDER TANKS

| Carateristici tehnice constructive | Technical construction data |
| --- | --- |
| - Norma : ASME VIII Div.1 | - Construction code: ASME VIII Div.1 |
| - Presiune de desing 12 bar | - Design pressure std. : 12 bar |
| - Presiune maxima de lucru:12 bar | - Max. working pressare std.: 12 bar |
| - Presiune de testare: 18 bar | - Test pressure std.: 18 bar |
| - Temperatura de design: -10° + 50°C | - Design temperature: -10° +50°C |
| La cerere rezervoarele se pot livra | - On request the tanks can be |
| cu diferite valori de presiune manufactured with different pressure |  |

values

| Caracteristici tehnice constructive | Technical construction data |
| --- | --- |
| Material | Materials |
| - Capac: ASTM A 516 GR. 70 | - Heads and vessel: ASTM A 516 GR.70 |
| - Flanse: ASTM A 105/A Gr.B | - Flanges: ASTM A 105/A Gr.B |
| - Teava: ASTM A 106 Gr.B | - Pipe: ASTM A 106 Gr.B |
| - Valva apa si spuma: ASTM A 105 cu sfera in AISI 304 | - Water and foam ball valve: ASTM A 105 with ball in AISI 304 |
| - Valva de drenaj si scurgere: Alama | - Drain and intercept valve: Brass |
| - Manometru: AISI 304 | - Pressare gauge: AISI 304 |
| - Duze apa si spuma:Otel inoxidabil | - Water and foam nozzles: St.steel |
| - Membrana: caiciuc armat | - Bladder: reinforced rubber |
| Ciclu de vopsire certificat C3H: | Certified painting cicle C3H: |
| - Preparare: sablare SA 2,5 | - Surface preparation: sand blasting SA 2,5 |
| - Prima mana: grund epoxidic bicomponent | - Primer: two component epoxy primer |
| - Final: two component acrylic polyurethane finish | - Finish: two component acrylic polyurethane finish |
| - Grosime finala 180 micron | - Tot. thickness 180 micron |

# TABELLA DIMENSIUNI

# DIMENSIONAL TABLE

| MODELLO MODEL | MISURE – DIMENSIONS |  |  |  |  | MAX. PESO VUOTO Kg. MAX. EMPTY WEIGHT Kg. | CAPACITA’ NOMINALE USG NOMINAL CAPACITY USG | CAPACITA’ NOMINALE Lt. NOMINAL CAPACITY Lt. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | D | E |  |  |  |
| FI-OPI-UL 50 | 500 | 1280 | 1382 | 550 | 600 | 382 | 50 | 190 |
| FI-OPI-UL 75 | 700 | 1055 | 1485 | 700 | 400 | 395 | 75 | 284 |
| FI-OPI-UL 100 | 700 | 1343 | 1370 | 660 | 600 | 426 | 100 | 379 |
| FI-OPI-UL 150 | 800 | 1482 | 1470 | 800 | 650 | 554 | 150 | 568 |
| FI-OPI-UL 200 | 800 | 1902 | 1470 | 800 | 900 | 602 | 200 | 757 |
| FI-OPI-UL 250 | 1000 | 1600 | 1654 | 900 | 660 | 653 | 250 | 947 |
| FI-OPI-UL 300 | 1000 | 1952 | 1654 | 900 | 800 | 685 | 300 | 1136 |
| FI-OPI-UL 350 | 1000 | 2103 | 1654 | 900 | 900 | 705 | 350 | 1325 |
| FI-OPI-UL 400 | 1000 | 2350 | 1654 | 900 | 1100 | 737 | 400 | 1514 |
| FI-OPI-UL 450 | 1000 | 2600 | 1654 | 900 | 1200 | 770 | 450 | 1704 |
| FI-OPI-UL 500 | 1100 | 2433 | 1756 | 1000 | 1200 | 877 | 500 | 1893 |
| FI-OPI-UL 600 | 1170 | 2576 | 1828 | 1000 | 1350 | 949 | 600 | 2271 |
| FI-OPI-UL 700 | 1270 | 2573 | 1930 | 1150 | 1350 | 980 | 700 | 2650 |

| MODELLO MODEL | MISURE – DIMENSIONS |  |  |  |  | MAX. PESO VUOTO Kg. MAX. EMPTY WEIGHT Kg. | CAPACITA’ NOMINALE USG NOMINAL CAPACITY USG | CAPACITA’ NOMINALE Lt. NOMINAL CAPACITY Lt. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | D | E |  |  |  |
| FI-OPI-UL 800 | 1270 | 2873 | 1930 | 1150 | 1400 | 1038 | 800 | 3028 |
| FI-OPI-UL 900 | 1360 | 2845 | 2024 | 1200 | 1400 | 1135 | 900 | 3407 |
| FI-OPI-UL 1000 | 1450 | 2808 | 2114 | 1250 | 1450 | 1253 | 1000 | 3785 |
| FI-OPI-UL 1100 | 1450 | 2978 | 2114 | 1250 | 1450 | 1296 | 1100 | 4164 |
| FI-OPI-UL 1200 | 1450 | 3278 | 2114 | 1250 | 1450 | 1374 | 1200 | 4542 |
| FI-OPI-UL 1300 | 1600 | 3008 | 2265 | 1400 | 1450 | 1591 | 1300 | 4921 |
| FI-OPI-UL 1400 | 1600 | 3188 | 2265 | 1400 | 1450 | 1650 | 1400 | 5299 |
| FI-OPI-UL 1500 | 1600 | 3378 | 2265 | 1400 | 1450 | 1711 | 1500 | 5678 |
| FI-OPI-UL 1600 | 1750 | 3107 | 2417 | 1500 | 1450 | 1775 | 1600 | 6056 |
| FI-OPI-UL 1700 | 1750 | 3267 | 2417 | 1500 | 1450 | 1831 | 1700 | 6435 |
| FI-OPI-UL 1800 | 1750 | 3407 | 2417 | 1500 | 1450 | 1880 | 1800 | 6813 |
| FI-OPI-UL 1900 | 1750 | 3577 | 2417 | 1500 | 1900 | 1941 | 1900 | 7192 |
| FI-OPI-UL 2000 | 1960 | 3132 | 2676 | 1700 | 1500 | 2383 | 2000 | 7570 |
| FI-OPI-UL 2200 | 1960 | 3382 | 2676 | 1700 | 1500 | 2506 | 2200 | 8327 |
| FI-OPI-UL 2400 | 2100 | 3286 | 2817 | 1850 | 1500 | 2674 | 2400 | 9084 |
| FI-OPI-UL 2600 | 2100 | 3476 | 2817 | 1850 | 1500 | 2776 | 2600 | 9841 |
| FI-OPI-UL 2800 | 2200 | 3438 | 2918 | 1950 | 1500 | 2891 | 2800 | 10598 |
| FI-OPI-UL 3000 | 2200 | 3648 | 2918 | 1950 | 1500 | 3008 | 3000 | 11355 |
| FI-OPI-UL 3200 | 2200 | 3858 | 2918 | 1950 | 1900 | 3124 | 3200 | 12112 |
| FI-OPI-UL 3400 | 2200 | 4078 | 2918 | 1950 | 1900 | 3247 | 3400 | 12869 |
| FI-OPI-UL 3600 | 2200 | 4278 | 2918 | 1950 | 2100 | 3357 | 3600 | 13626 |
| FI-OPI-UL 3800 | 2200 | 4478 | 2918 | 1950 | 2500 | 3467 | 3800 | 14383 |
| FI-OPI-UL 4000 | 2200 | 4678 | 2918 | 1950 | 2700 | 3579 | 4000 | 15140 |