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BLADDER TANK ORIZONTAL PENTRU SPUMA CU MEMBRANA CERTIFICAT UL 
UL LISTED HORIZONTAL FOAM BLADDER TANKS 
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	Carateristici tehnice constructive
	Technical construction data

	-  Norma : ASME VIII Div.1
	-	Construction code:  ASME VIII Div.1

	-  Presiune de desing 12 bar
	-	Design pressure std. : 12 bar

	-  Presiune maxima de lucru:12 bar
	-	Max. working pressare std.: 12 bar

	-  Presiune de testare: 18 bar
	-	Test pressure std.: 18 bar

	-  Temperatura de design: -10° + 50°C 
	-	Design temperature:  -10° +50°C

	     La cerere rezervoarele se pot livra 
	-	On request the tanks can be 

	       cu diferite valori de presiune 	manufactured with different pressure 


values

	Caracteristici tehnice constructive
	Technical construction data

	Material
	Materials

	-	Capac: ASTM A 516 GR. 70
	-	Heads and vessel: ASTM A 516 GR.70

	-	Flanse: ASTM A 105/A Gr.B
	-	Flanges: ASTM A 105/A Gr.B

	-     Teava: ASTM A 106 Gr.B
	-	Pipe: ASTM A 106 Gr.B

	-     Valva apa si spuma:          ASTM A 105 cu sfera in AISI 304
	-	Water and foam ball valve: 
        ASTM A 105 with ball in AISI 304

	-	    Valva de drenaj si scurgere: Alama 
	-	Drain and intercept valve: Brass

	-    Manometru: AISI 304 
	-	Pressare gauge: AISI 304 

	-   Duze apa si spuma:Otel inoxidabil
	-	Water and foam nozzles: St.steel

	-   Membrana: caiciuc armat
	-	Bladder: reinforced rubber

	Ciclu de vopsire certificat C3H:
	Certified painting cicle C3H:

	-   Preparare: sablare SA 2,5
	- Surface preparation: sand blasting SA 2,5

	-  Prima mana: grund epoxidic bicomponent
	-	Primer: two component epoxy primer

	-  Final: two component acrylic polyurethane finish
	-	Finish: two component acrylic polyurethane finish

	· Grosime finala 180 micron 
           
	-	Tot. thickness 180 micron 
           



TABELLA DIMENSIUNI
 DIMENSIONAL TABLE 
	MODELLO MODEL
	MISURE – DIMENSIONS 
	MAX. PESO VUOTO Kg. 
MAX. 
EMPTY 
WEIGHT Kg.
	CAPACITA’ 
NOMINALE USG 
NOMINAL 
CAPACITY USG
	CAPACITA’ 
NOMINALE 
Lt. 
NOMINAL 
CAPACITY 
Lt.

	
	A
	B
	C
	D
	E
	
	
	

	FI-OPI-UL 50
	500
	1280
	1382
	550
	600
	382
	50
	190

	FI-OPI-UL 75
	700
	1055
	1485
	700
	400
	395
	75
	284

	FI-OPI-UL 100
	700
	1343
	1370
	660
	600
	426
	100
	379

	FI-OPI-UL 150
	800
	1482
	1470
	800
	650
	554
	150
	568

	FI-OPI-UL 200
	800
	1902
	1470
	800
	900
	602
	200
	757

	FI-OPI-UL 250
	1000
	1600
	1654
	900
	660
	653
	250
	947

	FI-OPI-UL 300
	1000
	1952
	1654
	900
	800
	685
	300
	1136

	FI-OPI-UL 350
	1000
	2103
	1654
	900
	900
	705
	350
	1325

	FI-OPI-UL 400
	1000
	2350
	1654
	900
	1100
	737
	400
	1514

	FI-OPI-UL 450
	1000
	2600
	1654
	900
	1200
	770
	450
	1704

	FI-OPI-UL 500
	1100
	2433
	1756
	1000
	1200
	877
	500
	1893

	FI-OPI-UL 600
	1170
	2576
	1828
	1000
	1350
	949
	600
	2271

	FI-OPI-UL 700
	1270
	2573
	1930
	1150
	1350
	980
	700
	2650



	MODELLO MODEL
	MISURE – DIMENSIONS 
	MAX. PESO VUOTO Kg. 
MAX. 
EMPTY 
WEIGHT Kg.
	CAPACITA’ 
NOMINALE USG 
NOMINAL 
CAPACITY USG
	CAPACITA’ 
NOMINALE 
Lt. 
NOMINAL 
CAPACITY 
Lt.

	
	A
	B
	C
	D
	E
	
	
	

	FI-OPI-UL 800
	1270
	2873
	1930
	1150
	1400
	1038
	800
	3028

	FI-OPI-UL 900
	1360
	2845
	2024
	1200
	1400
	1135
	900
	3407

	FI-OPI-UL 1000
	1450
	2808
	2114
	1250
	1450
	1253
	1000
	3785

	FI-OPI-UL 1100
	1450
	2978
	2114
	1250
	1450
	1296
	1100
	4164

	FI-OPI-UL 1200
	1450
	3278
	2114
	1250
	1450
	1374
	1200
	4542

	FI-OPI-UL 1300
	1600
	3008
	2265
	1400
	1450
	1591
	1300
	4921

	FI-OPI-UL 1400
	1600
	3188
	2265
	1400
	1450
	1650
	1400
	5299

	FI-OPI-UL 1500
	1600
	3378
	2265
	1400
	1450
	1711
	1500
	5678

	FI-OPI-UL 1600
	1750
	3107
	2417
	1500
	1450
	1775
	1600
	6056

	FI-OPI-UL 1700
	1750
	3267
	2417
	1500
	1450
	1831
	1700
	6435

	FI-OPI-UL 1800
	1750
	3407
	2417
	1500
	1450
	1880
	1800
	6813

	FI-OPI-UL 1900
	1750
	3577
	2417
	1500
	1900
	1941
	1900
	7192

	FI-OPI-UL 2000
	1960
	3132
	2676
	1700
	1500
	2383
	2000
	7570

	FI-OPI-UL 2200
	1960
	3382
	2676
	1700
	1500
	2506
	2200
	8327

	FI-OPI-UL 2400
	2100
	3286
	2817
	1850
	1500
	2674
	2400
	9084

	FI-OPI-UL 2600
	2100
	3476
	2817
	1850
	1500
	2776
	2600
	9841

	FI-OPI-UL 2800
	2200
	3438
	2918
	1950
	1500
	2891
	2800
	10598

	FI-OPI-UL 3000
	2200
	3648
	2918
	1950
	1500
	3008
	3000
	11355

	FI-OPI-UL 3200
	2200
	3858
	2918
	1950
	1900
	3124
	3200
	12112

	FI-OPI-UL 3400
	2200
	4078
	2918
	1950
	1900
	3247
	3400
	12869

	FI-OPI-UL 3600
	2200
	4278
	2918
	1950
	2100
	3357
	3600
	13626

	FI-OPI-UL 3800
	2200
	4478
	2918
	1950
	2500
	3467
	3800
	14383

	FI-OPI-UL 4000
	2200
	4678
	2918
	1950
	2700
	3579
	4000
	15140
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