BLADDER TANK VERTICAL PENTRU SPUMA CU MEMBRANA INTERNA

VERTICAL FOAM BLADDER TANK INTERNAL MEMBRANE

Mod. FI-PI

| Caracteristici tehnice constructive | Technical construction data |
| --- | --- |
| - Norma: 2014/68/UE (Ex. PED 97/23/CE), ASME VIII Div.1 la cerere | - Construction code: 2014/68/UE (Ex. PED 97/23/CE), ASME VIII Div.1 on request |
| - Presiune de design: 12 bar | - Design pressure: 12 bar |
| - Presiune maxima de lucru: 12 bar | - Max working pressare: 12 bar |
| - Presiune de test: 18 bar | - Test pressure: 18 bar |
| - Temperatura de design: -10° + 50°C | - Design temperature: -10° +50°C |

Data Sheet N°50

| Caracteristici tehnice constructive | Technical construction data |
| --- | --- |
| Material | Materials |
| - Capac: P355 NH | - Shell and head: P355 NH |
| - Flanse: ASTM A 350 LF2 (UNI o ANSI) | - Flange: ASTM A 350 LF2 (UNI o ANSI) |
| - Teava: ASTM A 333 Gr.6 | - Pipe: ASTM A 333 Gr.6 |
| - Valva apa si spuma: ASTM A 105 cu sfera in AISI 304 | - Water and foam ball valve: ASTM A 105 with ball in AISI 304 |
| - Valva drenaj: Alama | - Drain and intercept valve: Brass |
| - Manometru: AISI 304 | - Pressare gauge: AISI 304 |
| - Duze apa si spuma: Otel inoxidabil | - Water and foam nozzles: Acciaio inox |
| - Membrana: Hypalon | - Bladder: Hypalon |
| Ciclu de vopsire | Painting cicle standard |
| - Preparare: sabbiatura SA 2,5 | - Surface preparation: sand blasting SA 2,5 |
| - Prima mana: Epoxivinilic 60 Microns | - Primer: Epoxivinilic 60 Microns |
| - Final: Email poliuretanic 60 Microns rosu RAL 3000 | - Finish: Enamel poliurethanic 60 Microns red RAL 3000 |

La cerere rezervoarele se pot furniza cu diferite valori de presiune

On request tanks can be supplied with different pressure values

TABEL DIMENSIUNI

DIMENSIONAL TABLE

| MODELLO MODEL | MISURE – DIMENSION |  |  |  | PESO MAX A VUOTO Kg. MAX EMPTY WEIGHT Kg. | CAPACITA’ Lt. CAPACITY Lt. |
| --- | --- | --- | --- | --- | --- | --- |
|  | A | C | D | E |  |  |
| FI-PI5 | 800 | 1955 | 624 | 650 | 415 | 500 |
| FI-PI6 | 800 | 2165 | 624 | 650 | 455 | 600 |
| FI-PI8 | 800 | 2565 | 624 | 650 | 490 | 800 |
| FI-PI10 | 1000 | 2248 | 790 | 750 | 525 | 1.000 |
| FI-PI15 | 1000 | 2838 | 790 | 750 | 615 | 1.500 |
| FI-PI20 | 1100 | 3109 | 864 | 800 | 880 | 2.000 |
| FI-PI25 | 1170 | 3339 | 914 | 800 | 965 | 2.500 |
| FI-PI30 | 1270 | 3372 | 984 | 860 | 995 | 3.000 |
| FI-PI35 | 1360 | 3412 | 1048 | 900 | 1095 | 3.500 |
| FI-PI40 | 1450 | 3450 | 1112 | 950 | 1300 | 4.000 |
| FI-PI45 | 1450 | 3715 | 1112 | 950 | 1380 | 4.500 |
| FI-PI50 | 1600 | 3536 | 1245 | 1050 | 1545 | 5.000 |
| FI-PI55 | 1600 | 3751 | 1245 | 1050 | 1620 | 5.500 |
| FI-PI60 | 1750 | 3603 | 1351 | 1150 | 1695 | 6.000 |
| FI-PI65 | 1750 | 3734 | 1351 | 1150 | 1735 | 6.500 |
| FI-PI70 | 1750 | 3953 | 1351 | 1150 | 1825 | 7.000 |
| FI-PI75 | 1750 | 4164 | 1351 | 1150 | 1900 | 7.500 |
| FI-PI80 | 1960 | 3749 | 1534 | 1200 | 2300 | 8.000 |
| FI-PI85 | 1960 | 3899 | 1534 | 1200 | 2370 | 8.500 |
| FI-PI90 | 2100 | 3821 | 1636 | 1300 | 2495 | 9.000 |
| FI-PI100 | 2200 | 3873 | 1707 | 1350 | 2630 | 10.000 |
| FI-PI110 | 2200 | 4003 | 1707 | 1350 | 2705 | 11.000 |
| FI-PI120 | 2200 | 4273 | 1707 | 1350 | 2860 | 12.000 |
| FI-PI150 | 2200 | 5173 | 1707 | 1350 | 3370 | 15.000 |